# Televised by:	Veit Environmental

Reviewed by:	Chris Carlson

Date Televised:	Wednesday, September 24th 2003

Tape No:	244  S: 02:10:55  E: ::

Time Starting:	1525

Time Finished:	1645

##### Weather Condition:

##### Precipitation:	[x] None [] Light [] Heavy    Temperature: 55F.

##### Conditions:	[x] Clear [] Partly Cloudy [] Cloudy [] Stormy

Line ID:		MH060219-MH060220

Location:

Length:		PL:  410’	’ Pipe Sections

Pipe Diameter:	PD:  10”

# Pipe Material:		[] PVC  [x] VCP  [] RCP [] Other: _________________________________

# Flow: 			[] None  [] Low  [] ½ pipe [] ¾ pipe

# Televise Direction:	[] Upstream  [x] Downstream

## Footage   Observations

| ### Footage | #### In-Service | Observation |
| --- | --- | --- |
| 000 | - | @ MH060220 |
| 007 | - | Set footage counter |
| 023 | No | Wye 10o/c |
| 025 | Yes | Wye 02o/c |
| 047 | No | Wye 10o/c |
| 049 | No | Wye 02o/c |
| 059 |  | Crack 12o/c |
| 067 | Yes | Wye 10o/c |
| 071 | No | Wye 10o/c |
| 073 | Yes | Wye 02o/c |
| 096 | No | Wye 10o/c |
| 098 | No | Wye 02o/c |
| 125 | No | Wye 02o/c |
| 147 | No | Wye 10o/c |
| 149 | No | Wye 02o/c |
| 160 | Yes | Tap 02o/c |
| 171 | No | Wye 10o/c |
| 174 | No | Wye 02o/c |
| 196 | No | Wye 10o/c |
| 198 | No | Wye 02o/c |
| 221 | Yes | Wye 10o/c |
| 223 | No | Wye 02o/c |
| 227 | Yes | Tap 03o/c Protruding |
| 248 | No | Wye 10o/c |
| 250 | No | Tap 03o/c |
| 272 | No | Wye 10o/c |
| 275 | No | Wye 02o/c |
| 299 | No | Wye 10o/c |
| 301 | Yes | Wye 02o/c |
| 324 | No | Wye 10o/c with Debris |
| 326 | No | Wye 02o/c |
| 330 | Yes | Tap 03o/c Protruding |
| 342 | Yes | Tap 10o/c |
| 348 | No | Wye 10o/c |
| 351 | No | Wye 02o/c |
| 373 | No | Wye 10o/c |
| 375 | No | Wye 02o/c |
| 380 | - | Underwater |
| 390 | - | Unable to Proceed due to Debris. Debris Seems to Form Dam Across Pipe |
|  |  | END |